# Month                                  .

Cooling Tower Water System:

| Month: | Day of Month | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Cooling Water Chemical Testing |
| Conductivity | < 800 umhos |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Phosphonate Test | 6 to 10 ppm |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Free Chlorine | 0.1 to 1.0 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Inventory |
| Cooling Treatment 1334 | Gallons |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Formula 4629 | Gallons |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |

Always verify water conductivity is in range before making chemical pump adjustments.  If water conductivity is low it will result in low chemical readings and visa versa.

Phosphonate Test

If < 6 ppm.  Verify conductivity is in range.  If in range, increase Cooling Treatment 1334 pump speed.

If >10 ppm. Verify conductivity is not high.  If in range, decrease Cooling Treatment 1334 pump speed.

Free Chlorine Test

If < 0.1 ppm.  Verify conductivity is in range.  If in range, increase Formula 4329 pump speed.

If >1.0 ppm. Verify conductivity is not high.  If in range, decrease Formula 4329 pump speed.

Notes: